## Slide 1: WP3 Infrastructure status and preview
P.Kuijer ETpathfinder workshop 2024-1-31

## Slide 2: Cleanroom Operation in 2023
The cleanroom continued to perform very well
  Extremely hot weather is a challenge for the dehumidifier
  System recovers without noticeable effect on the climate
  System recovers from power cut without problems
  We operate outside tender requirements (Narrower %RH, lower T)
  We have a new maintenance contract with Jansen cleanrooms
  Data logging is off for software development (and disk space)
Minor problems with leakage of water from the roof
  Addressed by UM facilities
Minor problems with sewage overflowing
  Addressed by UM facilities
Installed cooling unit for the optics lab in the ETpf corridor
  Does not affect the HVAC or available power

## Slide 3: 2023
Quite a lot of activities in the cleanroom
  Cryo system installation and LN2 tank outside
  A lot of progress on the vacuum system
  Adding tools to the small workshops
  Cleaning campaign was done in January.
    Thanks to those who helped!
  See specific WP sessions
Visits, public relations
  About 150 visits/year
  Government
  Companies
  General public
  We now limit visits to stakeholders
    check with Tim

## Slide 4: New skyjack
Scissor lift insufficient
Toucan 12E
  Up and over reach ~6m
  Can still manoeuvre almost everywhere
  We have limited the maximum speed for safety
  Using “socks” to protect the floor
  Trained personnel only! Check with Peter for availability.
Existing scissor lift
New Toucan 12E

## Slide 5: Safety
Safety analysis of vacuum system
  Safety of vacuum vessels evaluated
  Main issue is the risk of viewports breaking
  Under-pressure relief valves in the wall to be installed
    37000 m3/h at 50 Pa pressure
  Procedures for ensuring viewport quality
    Polarised light visual inspections
  Procedures for working with the vacuum system
    Minimum distance to viewport, …
  See the surfdrive for reports
Safety course required for working in the cleanroom
  Contact Tim and Dinesh for details
Cleanroom wall
Building wall

## Slide 6: Water
The HVAC has 20kW overcapacity under “standard Dutch weather conditions”
  With a lower setpoint and hot summers we get close to the limit
Forepump directly connected to primary cooling circuit
  Not critical temperature regulation in noisy area
For now two heat exchangers: 21 kW, 3.2 kW
  Racks and pumps in cleanroom
  Laser cooling specifications?
Pipes ordered, waiting for delivery
  We will install by ourselves using PEX tubes
See installation schedule

## Slide 7: Power distribution
We have wall sockets in cleanroom but not enough for all the equipment
Power will be distributed from the 125 kVA distribution panel in the noisy area
  Power rails above each rack and near pumps
Some delay because this is more expensive than anticipated
  Work with extension cords for now

## Slide 8
LinkedIn message by the Dutch minister of science
LinkedIn message by the Flemish minister of science

## Slide 9: Q&A
Suggestions infrastructure?
Suggestions general tools?
Suggestions safety features?