## Slide 1: LHCb VELO Upgrade II Progress meeting
1 JUL 2024
Yutaro Takahashi

## Slide 2: Roadmap pictures
Added beamline
Zoomed in version

## Slide 3: CO2 sublimation cooling
Update
  New needle valve installed by Martijn.
  Two tests performed to try to quantify cooling capacity.
Data to be analyzed
Early results
  Difficult to reproduce previous “successful” result
  Often Blocked channels
  Exit Temperature not below -58°C
  CO2 at exit has high vapour content (not so much ice)
  Increasing heat input leads to increased, but stable temperature.
    3,6W => -55°C, 6,4W => -53°C, 10W => -50°C
Analysis
  When the other channels get clogged, the ice formed can warp the soft gasket, leading to blockage of the channel by the gasket.
Some
  Change setting needle valve to allow lower flows (< 0,2 g/s)
  Try PTFE gasket (much stiffer)
\\ad.nikhef.nl\project\mt\project\LHCb\VELO Upgrade 2\CO2 Sublimation Cooling\20240625_Experiment_4

## Slide 4: Station design with extra ring
Targets:
  All modules to be placed at two independent angles (Rx and Ry)
  Each station at different angle?
  Minimum material
Challenges / Discussion
  A gap the inner and outer ring leads to open outer ring and should not be used.
  If the rotation point of the sensors is moved to the outside (to reduce material effects), this will influence the R1 of the detector.
Can we go for only one angle per sensor?
Gap
Gap
Rotation point
Beamline

## Slide 5: Layout
Some updates
  Number of stations is mainly determined by number of stations around IP.
  Taking 2 sigma: ±89,4 mm (=> total: ~180 mm), the pattern of the first 6 stations is repeated over the total length, with the given pitch (Dz).
  The acceptance can be optimized by evenly dividing the full IP region over the number of stations.
IP
IP+2σ
IP-2σ
 | Number of stations around IP | Max. pitch [mm] | Optimized pitch [mm] | Optimized acceptance angle
Concentric | 16 | 18,8 | 18 (=180/10) | 280 mrad
L-shape | 15 | 21,1 | 20 (=180/9) | 290 mrad
L-shape with extra ring | 12 | 30,7 | 30 (=180/6) | 276 mrad
L-shape with extra ring + extra station | 13 |  | 25,7 (=180/7) | 319 mrad

## Slide 6: Next week
Conceptual design of station with extra ring
(RGA setup)